JOB SAFETY ANALYSIS (JSA)

Wet Utilities Installation — Storm Sewer

| PROJECT NAME: | [Placeholder] | DATE: | [Placeholder] |
| --- | --- | --- | --- |
| PROJECT #: | [Placeholder] | PHASE: | [Placeholder] |
| WORK ACTIVITY: | Storm Sewer Installation — Trench Excavation, Pipe Laying, Inlet & Junction Box / Manhole Setting, Flared End Sections & Backfill |  | PREPARED BY: Safety Manager |
| COMPANY: | Wicker Construction Inc. | JSA TYPE: | Wet Utility Installation |

SCOPE OF WORK

This JSA covers all wet-utility installation activities for the Storm Sewer system, including: trenching and excavation, dewatering, bedding, pipe installation, structure/valve/hydrant setting, tie-ins, testing, backfill, and surface restoration. It is written for field execution and must be reviewed with the crew before work begins. This JSA is one of five (5) wet-utility JSAs: Storm Sewer, Sanitary Sewer, Industrial Waste / NCCW / INDW, Domestic Water, and Fire Water.

SCHEDULE

| MILESTONE | DATE | DESCRIPTION / POTENTIAL IMPACTS |
| --- | --- | --- |
| Predecessor Task | [Date] | Site clearing, erosion control, and access road preparation complete. |
| Start Date | [Date] | Begin trench excavation at downstream outfall / first structure. Delays impact upstream storm line sequencing. |
| Milestone #1 | [Date] | First storm structure (inlet / junction box / manhole) set and accepted. Initial run of pipe installed and surveyed. |
| Milestone #2 | [Date] | Trench advanced to mid-run. Dewatering operational if groundwater or stormwater encountered. |
| Milestone #3 | [Date] | All pipe joints complete and visually inspected. Watertight joints verified where required by spec. |
| Milestone #4 | [Date] | All structures set, frames/grates installed, flared end sections (FES) placed with riprap and geotextile. |
| Milestone #5 | [Date] | Final backfill and compaction complete. Compaction test reports submitted to engineer. |
| End Date | [Date] | Punch-list resolved. As-builts submitted. Site restored. Erosion control transitioned to permanent. |
| Successor Task | [Date] | Surface restoration, paving, curb & gutter, or connection to existing storm system / detention. |

CREW & CONTACTS

| TRADE PARTNER CONTACTS | NAME | PHONE NUMBER |
| --- | --- | --- |
| FOREMAN: | [Name] | [Phone] |
| SUPERINTENDENT: | [Name] | [Phone] |
| SAFETY PROFESSIONAL: | [Name] | [Phone] |
| WICKER SUPERINTENDENT: | [Name] | [Phone] |
| WICKER SAFETY PROFESSIONAL: | [Name] | [Phone] |
| CREW SPONSOR: | [Name] | [Phone] |

| REQUIRED CREW | PRODUCTIVITY REQUIREMENTS | WORK HOURS |
| --- | --- | --- |
| - 1 × Foreman - 1 × Superintendent - 2 × Equipment Operators (Excavator) - 1 × Equipment Operator (Loader/Compactor) - 2 × Laborers (Trench) - 1 × Pipe Layer / Grade Setter - 1 × Truck Driver (Spoils Haul-off) - 1 × Spotter / Flagger - 1 × Safety Observer (excavation > 4 ft) | - Pipe Installation: 100–150 LF/day - Structure Setting: 1–3 structures/day - Backfill & Compaction: Per lift per spec - Compaction Tests: Every 200 LF and each lift - Joint Inspection: Each joint before cover | - Standard: [Start] – [End] - Monday – Friday - Saturday as required - Overtime subject to owner approval - No work during lightning standdown |

MATERIALS

| MATERIAL | QTY | NOTES / STORAGE REQUIREMENTS |
| --- | --- | --- |
| HDPE Storm Pipe (dual-wall, per plan size & class) | Per plan LF | All storm pipe is HDPE. Store on flat, chocked ground. Protect from UV. Handle per mfr. instructions. |
| RCP (where specified at FES / heavy cover) | Per plan LF | Verify class (e.g., Class V) and bell direction. Store chocked. Inspect for cracks before install. |
| Precast Storm Structures (inlets, junction boxes, manholes) | Per plan EA | Delivered day of install. Set on firm bedding away from excavation edge. Verify Basin A / Basin C structure schedule. |
| Frames, Grates & Covers (HD, traffic-rated per plan) | Per plan EA | Verify casting load rating matches location (traffic vs. landscape). Store on pallets. |
| Crushed Stone Bedding (per spec / geotech) | Per plan TN | Stockpile in laydown area. Cover if rain expected. |
| Select Backfill (native or imported per spec) | Per plan CY | Verify approval with geotechnical engineer before placing. |
| Flared End Sections (FES) | Per plan EA | Match to pipe size. Install with riprap apron and geotextile per detail. |
| Riprap (per FES / outfall detail) | Per plan TN | 12" riprap over 8" stone bedding at FES per detail. Place over approved geotextile. |
| Geotextile Fabric (per spec — LADOTD Sec. 1019 Type D at temp. const. entrance; FES/riprap fabric per detail) | Per plan SY | Confirm fabric type by application. Do not substitute without engineer approval. |
| Joint Gaskets / Couplers (mfr. supplied) | Per joint | Keep shaded. Do not freeze. Use only mfr.-approved lubricant. |
| Non-Shrink Grout (structure connections) | As needed | Keep dry until use. Dispose of unused mixed material per SDS. |

TOOLS / EQUIPMENT

| TOOL / EQUIPMENT | QTY | NOTES |
| --- | --- | --- |
| Excavator — Long Reach (Cat 320 or equiv., trench bucket) | 1 | Inspect boom, bucket teeth, and hydraulic lines daily. |
| Excavator — Standard (Cat 308 or equiv., for backfill / setting) | 1 | Used for precise backfill placement and trench box advancement. |
| Steel Trench Box / Trench Shield (rated for excavation depth) | 1 set | Inspect spreaders and wales daily. Competent Person required. |
| Vibratory Plate Compactor (walk-behind, gas) | 2 | Use for compacting lifts adjacent to pipe. Do not compact directly on pipe. |
| Dewatering Pump (submersible, 3" or 4" discharge) | 2 | Discharge per permit — no direct surface discharge without approval. |
| Pipe Laser / Grade Laser (Topcon or equiv.) | 1 | Calibrate daily. Verify against benchmark. |
| Certified Lifting Bail / Slings (rated for heaviest pick) | 2 | Inspect before each lift. Match rating to heaviest section / pipe. |
| Confined Space Entry Kit (4-gas monitor, tripod, SRL, harness, winch) | 1 set | Required when personnel enter any structure or excavation >4 ft. Calibrate daily. |
| Wheel Loader (for bedding / backfill material staging) | 1 | Used to move material from stockpile to trench area. |
| Dump Trucks (spoils haul-off) | 2–3 | Coordinate with traffic control. Cover loads leaving site. |

HIGH-RISK ACTIVITY / ERROR-LIKELY

Attach specialized plans to the end of this document

| HIGH-RISK ACTIVITY | SPECIAL PLAN REQUIRED? |
| --- | --- |
| Excavation / Trenching exceeding 5 ft depth — Cave-in / Engulfment hazard | YES ☒ NO ☐ |
| Confined Space Entry — Junction boxes, manholes, and deep trench atmospheric hazards | YES ☒ NO ☐ |
| Work at / near open water, outfalls, and detention areas — Drowning / engulfment hazard | YES ☒ NO ☐ |
| Dewatering Operations — Stormwater / groundwater infiltration, trench instability, discharge permit compliance | YES ☒ NO ☐ |

REQUIRED PERMITS

| REQ'D | PERMIT / AUTHORIZATION |
| --- | --- |
| ☐ | Daily Dig / Excavation Permit (signed by Wicker Superintendent before any soil disruption) |
| ☐ | Confined Space Entry Permit (any structure or excavation >4 ft) |
| ☐ | Hot Work Permit (cutting / welding / grinding — if applicable) |
| ☐ | Dewatering / Stormwater Discharge Permit ([Permit No. / Agency]) |
| ☐ | Line Breaking / Energy Isolation (LOTO) Permit for tie-ins to live systems |
| ☐ | Locate / One-Call (811) Ticket — current and valid before excavation |
| ☐ | Crane / Critical Lift Permit (if pick exceeds standard rigging plan) |
| ☐ | Other (project-specific): ______________________________ |

EMERGENCY RESPONSE & STOP-WORK AUTHORITY

STOP-WORK AUTHORITY: Every worker has the unconditional right and duty to STOP WORK for any unsafe condition — trench instability, atmospheric alarm, utility strike, rigging concern, equipment fault, weather, or any uncertainty. Work does not resume until the condition is corrected and the Competent Person / Wicker Superintendent authorizes restart. No retaliation. Zero-incident mindset. EMERGENCY PROCEDURES: - Call 911. State exact site location / address: [Enter address & gate]. Send a runner to direct EMS. - Notify Wicker Superintendent and Wicker Safety immediately: [Phone]. - Muster Point: [Enter location]. Account for all personnel. Report headcount to Superintendent. - First Aid / AED location: [Enter]. Nearest hospital: [Enter name, address, phone]. - Trench collapse / engulfment: Do NOT enter to rescue. Call 911 / trained rescue. Shut down equipment, secure area. - Atmospheric alarm or confined-space emergency: Entrant exits; attendant initiates non-entry rescue; never enter to rescue. - Utility strike (gas/electric/comm): Stop work, evacuate, keep clear, call 911 and the utility owner. No equipment movement. - Spill / release: Stop source if safe, deploy spill kit / containment, report to Wicker Safety and per permit. - Severe weather / lightning: Standdown at 15 miles; resume 30 min after last strike. Exit trench.

CONTROLS REFERENCE — ENGINEERING · ADMINISTRATIVE · PPE

Applies to all tasks below. Task-specific controls are listed in the JHA.

| ENGINEERING CONTROLS | ADMINISTRATIVE CONTROLS | PPE (MINIMUM) |
| --- | --- | --- |
| - Trench box / shield, sloping, or shoring (>5 ft) - Spoils set back ≥4 ft from edge - Mechanical ventilation in confined spaces - Dewatering pumps & sumps - Ladder access within 25 ft, 3 ft above edge - Tag lines, restraints & thrust blocking - Trench plates / covers for after-hours - Backup alarms, cameras on equipment | - Competent Person daily trench inspection - Daily Dig & Confined Space permits - 811 locate; pothole; hand-dig within 3 ft - Pre-task huddle / JSA review & sign-on - 4-gas monitor calibrated & continuous - Trained/qualified operators & riggers - 15-ft exclusion zone & signage - Heat illness & lightning standdown plans | - Hard hat (ANSI Z89.1) - Hi-vis Class 2/3 vest - Safety glasses; face shield as needed - Steel/composite-toe boots - Cut-resistant (A4) gloves - Hearing protection near equipment - Harness/SRL near open edge & CSE - Task PPE: chem-resistant gloves/suit, FR, respirator per SDS/task |

QUALITY

Required inspections & frequency, critical tolerances, and key performance indicators.

| ITEM | REQUIREMENT |
| --- | --- |
| 1. Pipe Grade & Alignment | Verify pipe grade with laser at every joint. Tolerance per spec (typ. ±0.01 ft). Alignment checked every 50 LF. No reverse grades permitted on gravity storm. |
| 2. Bedding & Initial Backfill | Bedding placed and compacted to springline before joint is made. No large rocks or frozen material within 12" of HDPE pipe. Follow HDPE haunching requirements to prevent deflection. |
| 3. Joint Integrity | Each joint inspected for proper coupler/gasket engagement before covering. Watertight joints verified where specified. |
| 4. Structure Setting | Verify structure invert matches pipe invert. Connections grouted / booted. Frame, grate & cover set to finish grade per plan and traffic rating. |
| 5. FES & Outfall Protection | FES set to grade. Riprap (12") over stone (8") bedding placed over approved geotextile per detail BEFORE backfill. |
| 6. Compaction | Backfill compacted in lifts per spec. Third-party proctor testing. Minimum per spec (typ. 95% Standard Proctor). Reports submitted within 24 hrs. |

REFERENCE DOCUMENTS & DRAWINGS

- Approved Construction Drawings — Storm Drainage Plan & Profile Sheets (Sheet Nos. [X] through [X]); FES / outfall details; structure schedules (Basin A, Basin C) - Project Specifications — Division 33: Section 33 40 00 Storm Drainage Utilities - Geotechnical Report — Soils Investigation & Recommendations — [Geotechnical Firm, Date] - Engineer of Record — Bohler Engineering — applicable storm details and standards (TxDOT / NTCOG as specified) - OSHA 29 CFR 1926 Subpart P — Excavations (Trenching & Shoring) - OSHA 29 CFR 1926 Subpart AA — Confined Spaces in Construction - Wicker Construction Inc. — Site-Specific Health & Safety Plan (HASP) - Wicker Construction Inc. — Confined Space Entry Program & Permit - Wicker Construction Inc. — Excavation & Trenching Safety Plan - SWPPP / Stormwater & Dewatering Discharge Permit — [Permit No. / Agency] - Pipe Manufacturer Installation Manual (HDPE) — [Manufacturer Name]

JOB HAZARD ANALYSIS (JHA) — STORM SEWER INSTALLATION

OPERATIONAL STEPS IN LOGICAL ORDER. FOLLOW IN THE FIELD AS AN INSTRUCTION MANUAL: SETUP, OPERATION, INSPECTION, STOPPING POINTS, CLEANUP.

| # | WALK-THROUGH STEP | HAZARDS | RISK | CONTROLS & SAFE PROCEDURES |
| --- | --- | --- | --- | --- |
| 1 | All personnel informed of emergency procedures prior to performing any work on site. | - Worker injuries and exposures. - Hazardous flora and fauna. - Temperature extremes / heat stress. | LOW | - Emergency: Call 911. Know exact site location and address. Designated Muster Point staffed. Notify Wicker Safety immediately. - First Aid Kit location: [Enter Location]. Nearest hospital / urgent care posted: [Enter]. - All employees complete Site-Specific Safety Orientation before any work begins. - Flora/Fauna: Know poison ivy/oak/sumac, fire ants, snakes. Threatening animal — stop work, retreat, notify Supervisor and Safety. - Heat Stress: Water provided. Breaks in shade / A-C. Reference Wicker Heat Illness Prevention Plan. Buddy system in extreme heat. |
| 2 | Mobilize equipment (excavators, loader, trench box, compactor, dewatering pumps) to laydown yard via access road. | - Equipment/vehicle collisions on access road. - Poor road conditions or obstructions. - Dust impairing visibility. - Tipping/overturning on unstable ground. | MED | - Spotters and radio communication between all operators. - Inspect access road for stability and obstructions before mobilization. - Apply water / dust control as needed. - Keep delivery trucks centered — away from ditch and excavation edges. - Verify equipment weight does not exceed road / mat capacity. |
| 3 | Unload and stage equipment in designated laydown area. Equipment fueled prior to arriving on site. | - Slips, trips, falls on uneven ground. - Reduced visibility / blind spots during unloading. - Unauthorized personnel entering unloading zone. - Pinch points during chain/strap removal. | LOW | - Only trained / qualified personnel operate mobile equipment. - Flaggers / spotters required for every delivery. - Controlled access zone established opposite trailer. - Cut Level A4 gloves when unhooking safety chains. - Team lift required for items over 50 lbs or longer than 10 ft. |
| 4 | Superintendents / Forepersons inspect all equipment and work areas. Verify existing utilities. Complete Daily Dig Permit. | - Faulty or damaged equipment. - Exposure to moving equipment during inspection. - Slips, trips, falls. - Hydraulic leaks / spills. - Existing underground utilities struck. | MED | - Daily equipment maintenance check sheet completed and submitted to Wicker Superintendent. - GIS / One-Call (811) tickets current — all utilities marked and flagged before excavation. - Daily Dig Permit signed by Wicker Superintendent before any soil disruption. - LUAWA completed for excavation within 10 ft of any live utility. - No mechanical digging within 3 ft of known live utility — hand dig / pothole required. - Spill kits on site. Report spills immediately. - Lightning standdown at 15 miles. 30-min standdown from last strike. |
| 5 | Set up 15-ft exclusion zone around excavation area with weighted cones, red barrier chain, and signage. Establish Competent Person inspection protocol. | - Unauthorized personnel entering excavation zone. - Trench box not inspected before use. - Unidentified underground utilities in excavation path. | MED | - Delineate 15-ft exclusion zone. Post 'Excavation in Progress — Keep Out' signage. - Competent Person (CP) completes written daily excavation inspection BEFORE any worker enters trench. - All utilities physically potholed and located before excavator begins digging. - Field Engineer stakes pipe alignment and structure locations before excavation starts. - Daily Dig Permit signed and posted at excavation before work begins. |
| 6 | Begin trench excavation. Set spoils minimum 4 ft from edge of trench. Competent Person inspects trench before worker entry. | - Cave-in / trench wall collapse — engulfment hazard. - Workers struck by excavator or falling spoils. - Soil instability due to groundwater or poor soil type. - Equipment tipping from spoils surcharge near trench edge. | HIGH | - Competent Person classifies soil per OSHA 29 CFR 1926 Subpart P before excavation. - All excavations >5 ft require trench box, sloping, or shoring before worker entry. - Spoils minimum 4 ft from trench edge — no exceptions. - No workers in trench while excavator is actively digging. - Dewatering pump deployed if groundwater reaches excavation bottom. - Atmospheric monitoring required for all excavations >4 ft — test O₂, H₂S, CO, LEL before every entry. |
| 7 | Install trench box / trench shield. Establish fall protection, OSHA-compliant ladder access, and tie-off points before any workers enter excavation. | - Workers entering unshored excavation. - Trench box failure or improper installation. - Falls into open excavation. - Workers struck by trench box during installation. | MED | - Trench box inspected by Competent Person before installation — document inspection. - No worker entry until trench box is properly set and CP approves entry. - OSHA-compliant ladder extending 3 ft above trench edge installed within 25 ft of all workers. - SRL attached to certified tie-off point when near open excavation edge. - Laborers clear of area when trench box is being set or advanced. - Maintain spoils minimum 4 ft from trench edge at all times. |
| 8 | Prepare pipe bedding: place and compact bedding stone to required depth below pipe invert. Field Engineer verifies grade before pipe is set. | - Improper bedding causing pipe settlement or joint failure. - Workers struck by equipment placing bedding. - Grade error resulting in non-compliant pipe slope / cover. | MED | - Place bedding below pipe invert per spec. Set to laser / plan grade. - Field Engineer checks trench bottom elevation before any bedding is placed. - Workers in trench maintain visual and radio contact with excavator operator at all times. - Excavator operator uses slow, deliberate movements when placing bedding. - Pipe laser verified against established benchmark before bedding begins. |
| 9 | Place and connect HDPE storm pipe using excavator and certified rigging. Laborers guide pipe to grade and make coupler/gasket joints. | - Dropped load — pipe strikes workers in trench. - Pinch points at coupler / bell-and-spigot joints. - Rigging failure; HDPE pipe flotation in wet trench. - Pipe damaged (gouged/scored) reducing service life. | MED | - Tag lines required on all lifts. Workers clear of lift path and never under suspended load. - Use pipe slings / approved soft rigging for HDPE — no chains or bare cable directly on pipe. - Keep hands clear of joint pinch point when homing pipe. Use bar / come-along, not the excavator, to seat joints. - If trench has standing water, dewater before setting — HDPE will float. Restrain pipe until backfilled to prevent flotation. - Foreman inspects each joint for full engagement before covering. |
| 10 | Install flared end sections (FES) at outfalls; place geotextile, stone bedding, and riprap apron per detail. | - Working near open water / outfall — slip, fall, drowning. - Struck-by during riprap placement by excavator. - Manual handling of heavy riprap / fabric rolls. - Unstable saturated soil at outfall. | HIGH | - Establish footing and exclusion zone at outfall. Life ring / reach pole staged where standing water is present. - Place geotextile, then 8" stone, then 12" riprap in correct sequence BEFORE backfill — confirm against detail. - No workers under or beside the bucket during riprap placement. Operator uses slow, deliberate dumps. - Team lift fabric rolls; use machine to place riprap — do not hand-stack large stone. |
| 11 | Perform atmospheric monitoring and confined space entry (CSE) for joint inspection, grade confirmation, or structure work inside trench / structure. | - O₂ deficiency or toxic gas (H₂S, CO, methane) in trench or structure. - Engulfment if trench wall collapses during entry. - Worker unable to self-rescue from excavation. - Heat illness in confined, low-airflow trench. | HIGH | - Confined Space Entry Permit completed and posted before ANY worker enters excavation >4 ft or any structure. - 4-gas monitor (O₂, H₂S, CO, LEL) calibrated and tested daily. Test before entry and continuously during. - Acceptable atmosphere: O₂ 19.5–23.5%, H₂S <10 ppm, CO <35 ppm, LEL <10%. - Rescue plan established. Tripod, SRL, and rescue winch at entry point. Attendant at surface — NO entry to rescue. - Minimum 2 workers for confined space entry: 1 entrant, 1 attendant. - Ventilation fan deployed to maintain fresh air in deep / enclosed sections. - If alarm activates — immediate exit. Do not re-enter until source identified and cleared. |
| 12 | Perform initial backfill from pipe springline to 12" above pipe crown using approved material. Compact in lifts per spec. Third-party compaction testing. | - Pipe deflection or damage from improper backfill or compaction. - Workers struck by equipment during backfill. - Trench box movement damaging pipe during advancement. - Compaction equipment too close to pipe. | MED | - Initial backfill placed by hand or small equipment — no heavy equipment directly over pipe until adequate cover (per spec, typ. 24"). - Walk-behind vibratory plate for initial lifts. No jumping-jack compactor directly over pipe. - Third-party geotechnical inspector performs proctor testing per spec — every 200 LF and each lift. - Workers clear of excavator backfill zone. Radio and eye contact maintained. - Advance trench box in lifts — never pull box while workers are in trench. - CP re-inspects excavation walls after trench box is advanced. |
| 13 | Continue excavation, pipe installation, and backfill sequencing (repeat prior steps) as work progresses throughout the day. | - Complacency from repetitive tasks. - Fatigue increasing risk of errors. - Changing soil conditions as excavation advances. - Dewatering failure allowing water accumulation in trench. | MED | - Daily morning huddle: review JSA, JHA, and lessons learned from prior shift. - CP re-inspects trench at start of each day and after any rain event. - Dewatering pumps monitored throughout shift — dedicate one laborer to monitor pump operation. - Rotate workers in trench positions to reduce fatigue. Max 2-hour continuous trench work before break. - Foreman maintains constant awareness of trench conditions — STOP WORK if soil behavior changes. - Any near-miss or incident reported to Wicker Safety immediately — document and review before resuming. |
| 14 | Complete final backfill above pipe zone in compacted lifts using approved material. Loader / dozer and plate compactor used for upper lifts. | - Uneven / insufficient compaction causing surface settlement. - Equipment collision — loader and excavator in close proximity. - Workers struck by loader or compactor. - Compaction test failure requiring rework. | MED | - Clear radio communication between excavator and loader operators at all times. - Enforce no-walk zones around loader and compactor operation. - Minimum 1-ft clearance from placed pipe during compaction. - Third-party compaction testing at each lift per spec — do not advance to next lift until passing results received. - CP / Foreman signs off on each lift before proceeding. |
| 15 | End-of-day equipment refueling in designated fueling area. Secure all open trenches and structures before leaving site. | - Fire hazard during refueling. - Chemical spill — fuel or hydraulic fluid. - Public / unauthorized entry into open trench after hours. | MED | - All equipment completely shut off before refueling. No open flames within 50 ft. - Spill kit at fueling station. Fueling operator certified. Containment deployed under transfer hose. - Report all spills immediately. Document on spill report form. - Open excavations secured with trench plates, steel decking, or water-filled barriers after hours. - Warning lights and reflective signage placed around all excavations before leaving site. - Wicker Superintendent verifies site is secure before last person leaves. |

RISK KEY:  HIGH = serious injury/fatality potential — special plan & extra controls.   MED = controllable with standard controls.   LOW = routine.

KEY SITE-SPECIFIC HAZARDS & CONTROLS — Storm Sewer

| HAZARD | RISK | PRIMARY CONTROLS |
| --- | --- | --- |
| Cave-in / Engulfment (excavations >5 ft) | HIGH | CP daily inspection & soil classification; trench box/shield, sloping or shoring before entry; spoils ≥4 ft from edge; no entry while digging. |
| Confined Space (structures & deep trench) | HIGH | CSE permit; 4-gas monitor before & continuously; ventilation; tripod/SRL/winch; attendant — non-entry rescue only. |
| Work at open water / outfalls / detention | HIGH | Footing & exclusion zone at outfall; life ring/reach pole staged; correct geotextile→stone→riprap sequence before backfill. |
| HDPE pipe flotation in wet trench | MED | Dewater before setting; restrain pipe until backfilled; soft slings only — no chain/cable on pipe. |
| Struck-by / caught-between (equipment, loads) | MED | Spotters & radio; exclusion/no-walk zones; tag lines; certified rigging inspected each lift; never under suspended load. |
| Underground utility strike | HIGH | Current 811 ticket; pothole & hand-dig within 3 ft; LUAWA within 10 ft of live utility; stop/evacuate/call on strike. |
| Dewatering & discharge compliance | MED | Monitor pumps each shift; discharge per permit; no untreated/unpermitted surface discharge; treat as required. |
| Heat illness & weather | MED | Water/rest/shade; acclimatization; buddy system; lightning standdown at 15 mi, resume 30 min after last strike. |

APPROVAL SIGNATURES

| PREPARED BY — SAFETY MANAGER, Wicker Construction Inc. Signature: ______________________________ Print Name: _____________________________ Date: __________________ | WICKER SUPERINTENDENT Signature: ______________________________ Print Name: _____________________________ Date: __________________ |
| --- | --- |
| FOREMAN Signature: ______________________________ Print Name: _____________________________ Date: __________________ | WICKER SAFETY PROFESSIONAL Signature: ______________________________ Print Name: _____________________________ Date: __________________ |
| PROJECT MANAGER Signature: ______________________________ Print Name: _____________________________ Date: __________________ | OWNER / GC REPRESENTATIVE (as required) Signature: ______________________________ Print Name: _____________________________ Date: __________________ |

CREW REVIEW & SIGN-ON: By signing the attached crew sign-on sheet, each worker confirms this JSA was reviewed in the daily huddle, they understand the hazards and controls, and they understand their Stop-Work Authority.

REVISION LOG

| DATE | REV # | DESCRIPTION OF CHANGE | BY |
| --- | --- | --- | --- |
| [Date] | Rev 0 — Original | Initial JSA release — Storm Sewer wet-utility installation. | Safety Manager |